## Data Collected - Fixed DG P
Case 1 = Matpower implementation with NO snubbers and NO measurement resistors. Typhoon Diesel Genset operates in PQ mode.
Case 2 = Matpower implementation with ALL snubbers and NO measurement resistors. Typhoon Diesel Genset operates in PQ mode.
Case 3 = Matpower implementation with NO snubbers and ALL measurement resistors. Typhoon Diesel Genset operates in PQ mode.
Case 4 = Matpower implementation with ALL snubbers and ALL measurement resistors. Typhoon Diesel Genset operates in PQ mode.
Single Case = Typhoon Case only. Typhoon Diesel Genset operates in PV mode. V = 1pu and P = 1.5MW.
| Bus 1 is the SLACK bus - Stiff Grid | [5 empty] | Transmission lines are simple RL |  |  |  | Ts = 4e-6
| Bus 16 is the Diesel Genset Bus | [5 empty] | Voltage measurements are Line to Line
Case 1
MATPOWER - No snubbers, No measurement resistors | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.55 | 3.09 |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.594 | 2.8179 |  |  | 0% | - | 1.725% | 8.806%
2 | 0.998 | 0.023 |  |  |  |  | 2 | 13800 | 13780.9141 | 0.99862 | -0.0864 |  |  |  |  | 0.06182% | 475.7%
3 | 0.996 | -0.004 |  |  |  |  | 3 | 13800 | 13750.2441 | 0.99639 | -0.1728 |  |  |  |  | 0.03961% | 4220%
4 | 0.993 | -30.185 |  |  |  |  | 4 | 480 | 472.2735 | 0.9839 | -31.0226 |  |  |  |  | 0.9161% | 2.775%
5 | 0.985 | -30.85 |  |  |  |  | 5 | 480 | 472.9073 | 0.98522 | -30.9361 |  |  |  |  | 0.02269% | 0.2791%
6 | 0.952 | -31.25 |  |  |  |  | 6 | 480 | 456.856 | 0.95178 | -31.3682 |  |  |  |  | 0.02276% | 0.3782%
7 | 0.985 | -0.103 |  |  |  |  | 7 | 13800 | 13599.6182 | 0.98548 | -0.2592 |  |  |  |  | 0.04869% | 151.7%
8 | 0.985 | -0.105 |  |  |  |  | 8 | 13800 | 13597.8848 | 0.98535 | -0.2592 |  |  |  |  | 0.03594% | 146.9%
9 | 0.983 | -30.254 |  |  |  |  | 9 | 208 | 202.8204 | 0.9751 | -31.0226 |  |  |  |  | 0.8039% | 2.54% |  |  |  |  | Feeder1BansheeSimple.m
10 | 0.981 | -0.134 |  |  |  |  | 10 | 13800 | 13555.0967 | 0.98225 | -0.2592 |  |  |  |  | 0.1278% | 93.43%
11 | 0.964 | -31.749 |  |  |  |  | 11 | 4160 | 4037.2976 | 0.9705 | -31.3682 |  |  |  |  | 0.6747% | 1.199%
12 | 0.951 | -62.803 |  |  |  |  | 12 | 480 | 457.9556 | 0.95407 | -62.7364 |  |  |  |  | 0.3233% | 0.106%
13 | 0.954 | -62.559 |  |  |  |  | 13 | 480 | 459.9652 | 0.95826 | -62.3044 |  |  |  |  | 0.4466% | 0.407%
14 | 0.963 | -31.76 |  |  |  |  | 14 | 4160 | 4033.5256 | 0.9696 | -31.3682 |  |  |  |  | 0.6851% | 1.234%
15 | 0.999 | 0.105 |  |  |  |  | 15 | 13800 | 13788.666 | 0.99918 | 0 |  |  |  |  | 0.01789% | -
16 | 1 | 0.318 | 1.5 | -0.98 |  |  | 16 | 13800 | 13800.3604 | 1 | 0.2016 | 1.5004 | -1.0406 |  |  | 0.002612% | 36.6% | 0.02667% | 6.184%
17 | 0.999 | 0.104 |  |  |  |  | 17 | 13800 | 13786.584 | 0.99903 | -0.0864 |  |  |  |  | 0.002785% | 183.1%
18 | 0.998 | -29.929 |  |  |  |  | 18 | 480 | 479.1822 | 0.9983 | -30.072 |  |  |  |  | 0.02968% | 0.4778%
19 | 0.933 | -30.703 |  |  |  |  | 19 | 480 | 447.7018 | 0.93271 | -30.8497 |  |  |  |  | 0.03086% | 0.4778%
|  |  | 4.05 | 2.11 | [7 empty] | 4.0944 | 1.7773 |  |  |  |  | -1.096% | 15.77% | 4.5667 | 4.4635
Case 2
MATPOWER - All Snubbers, No measurement resistors | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.55 | 2.9 |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.5938 | 2.9092 |  |  | 0% | - | 1.718% | 0.3172%
2 | 0.998 | 0.019 |  |  |  |  | 2 | 13800 | 13780.5908 | 0.99859 | -0.0864 |  |  |  |  | 0.05947% | 554.7%
3 | 0.996 | -0.008 |  |  |  |  | 3 | 13800 | 13749.9219 | 0.99637 | -0.1728 |  |  |  |  | 0.03726% | 2060%
4 | 0.994 | -30.189 |  |  |  |  | 4 | 480 | 472.2625 | 0.98388 | -31.0226 |  |  |  |  | 1.018% | 2.761%
5 | 0.985 | -30.854 |  |  |  |  | 5 | 480 | 472.8962 | 0.9852 | -30.9361 |  |  |  |  | 0.02035% | 0.2661%
6 | 0.952 | -31.254 |  |  |  |  | 6 | 480 | 456.8452 | 0.95176 | -31.3682 |  |  |  |  | 0.02512% | 0.3654%
7 | 0.985 | -0.127 |  |  |  |  | 7 | 13800 | 13599.2988 | 0.98546 | -0.2592 |  |  |  |  | 0.04634% | 104.1% |  |  |  |  | feeder1Banshee.m
8 | 0.985 | -0.128 |  |  |  |  | 8 | 13800 | 13597.5664 | 0.98533 | -0.2592 |  |  |  |  | 0.03359% | 102.5%
9 | 0.983 | -30.278 |  |  |  |  | 9 | 208 | 202.8156 | 0.97507 | -31.0226 |  |  |  |  | 0.8062% | 2.459%
10 | 0.982 | -0.164 |  |  |  |  | 10 | 13800 | 13554.7793 | 0.98223 | -0.2592 |  |  |  |  | 0.02346% | 58.05%
11 | 0.964 | -31.779 |  |  |  |  | 11 | 4160 | 4037.2029 | 0.97048 | -31.3682 |  |  |  |  | 0.6724% | 1.293%
12 | 0.951 | -62.833 |  |  |  |  | 12 | 480 | 457.9449 | 0.95405 | -62.7364 |  |  |  |  | 0.3209% | 0.1537%
13 | 0.954 | -62.59 |  |  |  |  | 13 | 480 | 459.9545 | 0.95824 | -62.3044 |  |  |  |  | 0.4443% | 0.4563%
14 | 0.963 | -31.79 |  |  |  |  | 14 | 4160 | 4033.4312 | 0.96957 | -31.3682 |  |  |  |  | 0.6827% | 1.327%
15 | 0.999 | 0.1 |  |  |  |  | 15 | 13800 | 13787.7432 | 0.99911 | 0 |  |  |  |  | 0.01119% | -
16 | 1 | 0.317 | 1.5 | -1.1 |  |  | 16 | 13800 | 13797.2949 | 0.9998 | 0.2592 | 1.5001 | -1.1304 |  |  | 0.0196% | 18.23% | 0.006667% | 2.764%
17 | 0.999 | 0.1 |  |  |  |  | 17 | 13800 | 13785.6621 | 0.99896 | -0.0864 |  |  |  |  | 0.003902% | 186.4%
18 | 0.998 | -29.934 |  |  |  |  | 18 | 480 | 479.1501 | 0.99823 | -30.072 |  |  |  |  | 0.02298% | 0.461%
19 | 0.933 | -30.707 |  |  |  |  | 19 | 480 | 447.6718 | 0.93265 | -30.8497 |  |  |  |  | 0.03756% | 0.4647%
|  |  | 4.05 | 1.8 | [7 empty] | 4.0939 | 1.7788 |  |  |  |  | 1.084% | 1.178% | 4.432 | 4.4636
Case 3
MATPOWER - No snubbers, All measurement resistors | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.59 | 3.08 |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.5937 | 2.7374 |  |  | 0% | - | 0.1429% | 11.12%
2 | 0.998 | 0.022 |  |  |  |  | 2 | 13800 | 13781.2129 | 0.99864 | -0.0864 |  |  |  |  | 0.06399% | 492.7%
3 | 0.996 | -0.005 |  |  |  |  | 3 | 13800 | 13750.542 | 0.99642 | -0.1728 |  |  |  |  | 0.04178% | 3356%
4 | 0.993 | -30.186 |  |  |  |  | 4 | 480 | 472.2838 | 0.98392 | -31.0226 |  |  |  |  | 0.9139% | 2.771%
5 | 0.985 | -30.852 |  |  |  |  | 5 | 480 | 472.9176 | 0.98525 | -30.9361 |  |  |  |  | 0.02487% | 0.2726%
6 | 0.952 | -31.252 |  |  |  |  | 6 | 480 | 456.8658 | 0.9518 | -31.3682 |  |  |  |  | 0.02061% | 0.3718%
7 | 0.985 | -0.106 |  |  |  |  | 7 | 13800 | 13599.9131 | 0.9855 | -0.2592 |  |  |  |  | 0.05086% | 144.5% |  |  |  |  | feeder1BansheeNoSnubbers.m
8 | 0.985 | -0.108 |  |  |  |  | 8 | 13800 | 13598.1797 | 0.98538 | -0.2592 |  |  |  |  | 0.03811% | 140%
9 | 0.983 | -30.257 |  |  |  |  | 9 | 208 | 202.8248 | 0.97512 | -31.0226 |  |  |  |  | 0.8017% | 2.53%
10 | 0.981 | -0.137 |  |  |  |  | 10 | 13800 | 13555.3906 | 0.98227 | -0.2592 |  |  |  |  | 0.1299% | 89.2%
11 | 0.964 | -31.753 |  |  |  |  | 11 | 4160 | 4037.385 | 0.97053 | -31.3682 |  |  |  |  | 0.6769% | 1.212%
12 | 0.951 | -62.807 |  |  |  |  | 12 | 480 | 457.9655 | 0.95409 | -62.7364 |  |  |  |  | 0.3254% | 0.1124%
13 | 0.954 | -62.563 |  |  |  |  | 13 | 480 | 459.9752 | 0.95828 | -62.3908 |  |  |  |  | 0.4488% | 0.2752%
14 | 0.963 | -31.764 |  |  |  |  | 14 | 4160 | 4033.613 | 0.96962 | -31.3682 |  |  |  |  | 0.6873% | 1.246%
15 | 0.999 | 0.104 |  |  |  |  | 15 | 13800 | 13789.5186 | 0.99924 | 0 |  |  |  |  | 0.02407% | -
16 | 1 | 0.315 | 1.5 | -0.97 |  |  | 16 | 13800 | 13803.1816 | 1.0002 | 0.1728 | 1.4996 | -0.9595 |  |  | 0.02306% | 45.14% | 0.02667% | 1.082%
17 | 0.999 | 0.103 |  |  |  |  | 17 | 13800 | 13787.4365 | 0.99909 | -0.0864 |  |  |  |  | 0.008969% | 183.9%
18 | 0.998 | -29.931 |  |  |  |  | 18 | 480 | 479.2118 | 0.99836 | -30.072 |  |  |  |  | 0.03586% | 0.4711%
19 | 0.932 | -30.704 |  |  |  |  | 19 | 480 | 447.7294 | 0.93277 | -30.8497 |  |  |  |  | 0.08257% | 0.4745%
|  |  | 4.09 | 2.11 | [7 empty] | 4.0933 | 1.7779 |  |  |  |  | 0.08068% | 15.74% | 4.6022 | 4.4627 |  | 0.0033 | -0.3321
Case 4
MATPOWER - ALL snubbers, All measurement resistors | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.59 | 2.89 |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.5936 | 2.8791 |  |  | 0% | - | 0.139% | 0.3772%
2 | 0.998 | 0.018 |  |  |  |  | 2 | 13800 | 13780.7012 | 0.9986 | -0.0864 |  |  |  |  | 0.06027% | 580%
3 | 0.996 | -0.009 |  |  |  |  | 3 | 13800 | 13750.0312 | 0.99638 | -0.1728 |  |  |  |  | 0.03806% | 1820%
4 | 0.994 | -30.19 |  |  |  |  | 4 | 480 | 472.2662 | 0.98389 | -31.0226 |  |  |  |  | 1.017% | 2.758%
5 | 0.985 | -30.855 |  |  |  |  | 5 | 480 | 472.9 | 0.98521 | -30.9361 |  |  |  |  | 0.02115% | 0.2628%
6 | 0.952 | -31.255 |  |  |  |  | 6 | 480 | 456.8489 | 0.95177 | -31.3682 |  |  |  |  | 0.02431% | 0.3622%
7 | 0.985 | -0.13 |  |  |  |  | 7 | 13800 | 13599.4082 | 0.98546 | -0.2592 |  |  |  |  | 0.04714% | 99.38%
8 | 0.985 | -0.132 |  |  |  |  | 8 | 13800 | 13597.6748 | 0.98534 | -0.2592 |  |  |  |  | 0.03439% | 96.36%
9 | 0.983 | -30.281 |  |  |  |  | 9 | 208 | 202.8173 | 0.97508 | -31.0226 |  |  |  |  | 0.8054% | 2.449% |  |  |  |  | Feeder1BansheeFULL.m
10 | 0.982 | -0.167 |  |  |  |  | 10 | 13800 | 13554.8877 | 0.98224 | -0.2592 |  |  |  |  | 0.02426% | 55.21%
11 | 0.964 | -31.783 |  |  |  |  | 11 | 4160 | 4037.2351 | 0.97049 | -31.3682 |  |  |  |  | 0.6732% | 1.305%
12 | 0.951 | -62.837 |  |  |  |  | 12 | 480 | 457.9485 | 0.95406 | -62.7364 |  |  |  |  | 0.3217% | 0.1601%
13 | 0.954 | -62.593 |  |  |  |  | 13 | 480 | 459.9581 | 0.95825 | -62.3044 |  |  |  |  | 0.4451% | 0.4611%
14 | 0.963 | -31.794 |  |  |  |  | 14 | 4160 | 4033.4634 | 0.96958 | -31.3682 |  |  |  |  | 0.6835% | 1.339%
15 | 0.999 | 0.099 |  |  |  |  | 15 | 13800 | 13788.0586 | 0.99913 | 0 |  |  |  |  | 0.01348% | -
16 | 1 | 0.315 | 1.5 | -1.09 |  |  | 16 | 13800 | 13798.3389 | 0.99988 | 0.2592 | 1.5002 | -1.1007 |  |  | 0.01204% | 17.71% | 0.01333% | 0.9817%
17 | 0.999 | 0.098 |  |  |  |  | 17 | 13800 | 13785.9766 | 0.99898 | -0.0864 |  |  |  |  | 0.00162% | 188.2%
18 | 0.998 | -29.935 |  |  |  |  | 18 | 480 | 479.1611 | 0.99825 | -30.072 |  |  |  |  | 0.02528% | 0.4577%
19 | 0.933 | -30.709 |  |  |  |  | 19 | 480 | 447.682 | 0.93267 | -30.8497 |  |  |  |  | 0.03528% | 0.4582%
|  |  | 4.09 | 1.8 | [7 empty] | 4.0938 | 1.7784 |  |  |  |  | 0.09291% | 1.2% | 4.4686 | 4.4634 |  | 0.0038 | -0.0216
Matpower Case 1 vs Typhoon Single Case (DG in PV mode. V = 1pu and P = 1.5MW)
MATPOWER - NO snubbers, NO measurement resistors | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.55 | 3.09 |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.5953 | 2.7886 |  |  | 0% | - | 1.776% | 9.754%
2 | 0.998 | 0.023 |  |  |  |  | 2 | 13800 | 13781.03 | 0.99863 | -0.0864 |  |  |  |  | 0.06266% | 475.7%
3 | 0.996 | -0.004 |  |  |  |  | 3 | 13800 | 13750.36 | 0.9964 | -0.1728 |  |  |  |  | 0.04045% | 4220%
4 | 0.993 | -30.185 |  |  |  |  | 4 | 480 | 472.36 | 0.98408 | -31.0226 |  |  |  |  | 0.898% | 2.775%
5 | 0.985 | -30.85 |  |  |  |  | 5 | 480 | 472.91 | 0.98523 | -30.9361 |  |  |  |  | 0.02327% | 0.2791%
6 | 0.952 | -31.25 |  |  |  |  | 6 | 480 | 456.86 | 0.95179 | -31.3682 |  |  |  |  | 0.02188% | 0.3782%
7 | 0.985 | -0.103 |  |  |  |  | 7 | 13800 | 13599.73 | 0.98549 | -0.2592 |  |  |  |  | 0.04951% | 151.7%
8 | 0.985 | -0.105 |  |  |  |  | 8 | 13800 | 13598 | 0.98536 | -0.2592 |  |  |  |  | 0.03678% | 146.9%
9 | 0.983 | -30.254 |  |  |  |  | 9 | 208 | 202.82 | 0.9751 | -31.0226 |  |  |  |  | 0.8041% | 2.54%
10 | 0.981 | -0.134 |  |  |  |  | 10 | 13800 | 13555.21 | 0.98226 | -0.2592 |  |  |  |  | 0.1286% | 93.43%
11 | 0.964 | -31.749 |  |  |  |  | 11 | 4160 | 4037.33 | 0.97051 | -31.3682 |  |  |  |  | 0.6755% | 1.199%
12 | 0.951 | -62.803 |  |  |  |  | 12 | 480 | 457.96 | 0.95408 | -62.7364 |  |  |  |  | 0.3242% | 0.106%
13 | 0.954 | -62.559 |  |  |  |  | 13 | 480 | 459.97 | 0.95827 | -62.3908 |  |  |  |  | 0.4477% | 0.2689%
14 | 0.963 | -31.76 |  |  |  |  | 14 | 4160 | 4033.56 | 0.96961 | -31.3682 |  |  |  |  | 0.686% | 1.234%
15 | 0.999 | 0.105 |  |  |  |  | 15 | 13800 | 13788.99 | 0.9992 | 0 |  |  |  |  | 0.02024% | -
16 | 1 | 0.318 | 1.5 | -0.98 |  |  | 16 | 13800 | 13801.45 | 1.0001 | 0.1728 | 1.5004 | -1.0084 |  |  | 0.01051% | 45.66% | 0.02667% | 2.898%
17 | 0.999 | 0.104 |  |  |  |  | 17 | 13800 | 13786.91 | 0.99905 | -0.086414 |  |  |  |  | 0.00515% | 183.1%
18 | 0.998 | -29.929 |  |  |  |  | 18 | 480 | 479.19 | 0.99831 | -30.072 |  |  |  |  | 0.03131% | 0.4778%
19 | 0.933 | -30.703 |  |  |  |  | 19 | 480 | 447.71 | 0.93273 | -30.8497 |  |  |  |  | 0.02903% | 0.4778%
|  |  | 4.05 | 2.11 | [7 empty] | 4.0957 | 1.7802 |  |  |  |  | 1.128% | 15.63% | 4.5667 | 4.4659
Matpower Case 2 vs Typhoon Single Case (DG in PV mode. V = 1pu and P = 1.5MW)
MATPOWER - ALL snubbers, NO measurement resistors | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.55 | 2.9 |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.5953 | 2.7886 |  |  | 0% | - | 1.776% | 3.841%
2 | 0.998 | 0.019 |  |  |  |  | 2 | 13800 | 13781.03 | 0.99863 | -0.0864 |  |  |  |  | 0.06266% | 554.7%
3 | 0.996 | -0.008 |  |  |  |  | 3 | 13800 | 13750.36 | 0.9964 | -0.1728 |  |  |  |  | 0.04045% | 2060%
4 | 0.994 | -30.189 |  |  |  |  | 4 | 480 | 472.36 | 0.98408 | -31.0226 |  |  |  |  | 0.9977% | 2.761%
5 | 0.985 | -30.854 |  |  |  |  | 5 | 480 | 472.91 | 0.98523 | -30.9361 |  |  |  |  | 0.02327% | 0.2661%
6 | 0.952 | -31.254 |  |  |  |  | 6 | 480 | 456.86 | 0.95179 | -31.3682 |  |  |  |  | 0.02188% | 0.3654%
7 | 0.985 | -0.127 |  |  |  |  | 7 | 13800 | 13599.73 | 0.98549 | -0.2592 |  |  |  |  | 0.04951% | 104.1%
8 | 0.985 | -0.128 |  |  |  |  | 8 | 13800 | 13598 | 0.98536 | -0.2592 |  |  |  |  | 0.03678% | 102.5%
9 | 0.983 | -30.278 |  |  |  |  | 9 | 208 | 202.82 | 0.9751 | -31.0226 |  |  |  |  | 0.8041% | 2.459%
10 | 0.982 | -0.164 |  |  |  |  | 10 | 13800 | 13555.21 | 0.98226 | -0.2592 |  |  |  |  | 0.02664% | 58.05%
11 | 0.964 | -31.779 |  |  |  |  | 11 | 4160 | 4037.33 | 0.97051 | -31.3682 |  |  |  |  | 0.6755% | 1.293%
12 | 0.951 | -62.833 |  |  |  |  | 12 | 480 | 457.96 | 0.95408 | -62.7364 |  |  |  |  | 0.3242% | 0.1537%
13 | 0.954 | -62.59 |  |  |  |  | 13 | 480 | 459.97 | 0.95827 | -62.3908 |  |  |  |  | 0.4477% | 0.3183%
14 | 0.963 | -31.79 |  |  |  |  | 14 | 4160 | 4033.56 | 0.96961 | -31.3682 |  |  |  |  | 0.686% | 1.327%
15 | 0.999 | 0.1 |  |  |  |  | 15 | 13800 | 13788.99 | 0.9992 | 0 |  |  |  |  | 0.02024% | -
16 | 1 | 0.317 | 1.5 | -1.1 |  |  | 16 | 13800 | 13801.45 | 1.0001 | 0.1728 | 1.5004 | -1.0084 |  |  | 0.01051% | 45.49% | 0.02667% | 8.327%
17 | 0.999 | 0.1 |  |  |  |  | 17 | 13800 | 13786.91 | 0.99905 | -0.086414 |  |  |  |  | 0.00515% | 186.4%
18 | 0.998 | -29.934 |  |  |  |  | 18 | 480 | 479.19 | 0.99831 | -30.072 |  |  |  |  | 0.03131% | 0.461%
19 | 0.933 | -30.707 |  |  |  |  | 19 | 480 | 447.71 | 0.93273 | -30.8497 |  |  |  |  | 0.02903% | 0.4647%
|  |  | 4.05 | 1.8 | [7 empty] | 4.0957 | 1.7802 |  |  |  |  | 1.128% | 1.1% | 4.432 | 4.4659
Matpower Case 3 vs Typhoon Single Case (DG in PV mode. V = 1pu and P = 1.5MW)
MATPOWER - NO snubbers, All measurement resistors | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.59 | 3.08 |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.5953 | 2.7886 |  |  | 0% | - | 0.2046% | 9.461%
2 | 0.998 | 0.022 |  |  |  |  | 2 | 13800 | 13781.03 | 0.99863 | -0.0864 |  |  |  |  | 0.06266% | 492.7%
3 | 0.996 | -0.005 |  |  |  |  | 3 | 13800 | 13750.36 | 0.9964 | -0.1728 |  |  |  |  | 0.04045% | 3356%
4 | 0.993 | -30.186 |  |  |  |  | 4 | 480 | 472.36 | 0.98408 | -31.0226 |  |  |  |  | 0.898% | 2.771%
5 | 0.985 | -30.852 |  |  |  |  | 5 | 480 | 472.91 | 0.98523 | -30.9361 |  |  |  |  | 0.02327% | 0.2726%
6 | 0.952 | -31.252 |  |  |  |  | 6 | 480 | 456.86 | 0.95179 | -31.3682 |  |  |  |  | 0.02188% | 0.3718%
7 | 0.985 | -0.106 |  |  |  |  | 7 | 13800 | 13599.73 | 0.98549 | -0.2592 |  |  |  |  | 0.04951% | 144.5%
8 | 0.985 | -0.108 |  |  |  |  | 8 | 13800 | 13598 | 0.98536 | -0.2592 |  |  |  |  | 0.03678% | 140%
9 | 0.983 | -30.257 |  |  |  |  | 9 | 208 | 202.82 | 0.9751 | -31.0226 |  |  |  |  | 0.8041% | 2.53%
10 | 0.981 | -0.137 |  |  |  |  | 10 | 13800 | 13555.21 | 0.98226 | -0.2592 |  |  |  |  | 0.1286% | 89.2%
11 | 0.964 | -31.753 |  |  |  |  | 11 | 4160 | 4037.33 | 0.97051 | -31.3682 |  |  |  |  | 0.6755% | 1.212%
12 | 0.951 | -62.807 |  |  |  |  | 12 | 480 | 457.96 | 0.95408 | -62.7364 |  |  |  |  | 0.3242% | 0.1124%
13 | 0.954 | -62.563 |  |  |  |  | 13 | 480 | 459.97 | 0.95827 | -62.3908 |  |  |  |  | 0.4477% | 0.2752%
14 | 0.963 | -31.764 |  |  |  |  | 14 | 4160 | 4033.56 | 0.96961 | -31.3682 |  |  |  |  | 0.686% | 1.246%
15 | 0.999 | 0.104 |  |  |  |  | 15 | 13800 | 13788.99 | 0.9992 | 0 |  |  |  |  | 0.02024% | -
16 | 1 | 0.315 | 1.5 | -0.97 |  |  | 16 | 13800 | 13801.45 | 1.0001 | 0.1728 | 1.5004 | -1.0084 |  |  | 0.01051% | 45.14% | 0.02667% | 3.959%
17 | 0.999 | 0.103 |  |  |  |  | 17 | 13800 | 13786.91 | 0.99905 | -0.086414 |  |  |  |  | 0.00515% | 183.9%
18 | 0.998 | -29.931 |  |  |  |  | 18 | 480 | 479.19 | 0.99831 | -30.072 |  |  |  |  | 0.03131% | 0.4711%
19 | 0.932 | -30.704 |  |  |  |  | 19 | 480 | 447.71 | 0.93273 | -30.8497 |  |  |  |  | 0.07824% | 0.4745%
|  |  | 4.09 | 2.11 | [7 empty] | 4.0957 | 1.7802 |  |  |  |  | 0.1394% | 15.63% | 4.6022 | 4.4659
Matpower Case 4 vs Typhoon Single Case (DG in PV mode. V = 1pu and P = 1.5MW)
MATPOWER - ALL snubbers, All measurement resistors | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.59 | 2.89 |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.5953 | 2.7886 |  |  | 0% | - | 0.2046% | 3.509%
2 | 0.998 | 0.018 |  |  |  |  | 2 | 13800 | 13781.03 | 0.99863 | -0.0864 |  |  |  |  | 0.06266% | 580%
3 | 0.996 | -0.009 |  |  |  |  | 3 | 13800 | 13750.36 | 0.9964 | -0.1728 |  |  |  |  | 0.04045% | 1820%
4 | 0.994 | -30.19 |  |  |  |  | 4 | 480 | 472.36 | 0.98408 | -31.0226 |  |  |  |  | 0.9977% | 2.758%
5 | 0.985 | -30.855 |  |  |  |  | 5 | 480 | 472.91 | 0.98523 | -30.9361 |  |  |  |  | 0.02327% | 0.2628%
6 | 0.952 | -31.255 |  |  |  |  | 6 | 480 | 456.86 | 0.95179 | -31.3682 |  |  |  |  | 0.02188% | 0.3622%
7 | 0.985 | -0.13 |  |  |  |  | 7 | 13800 | 13599.73 | 0.98549 | -0.2592 |  |  |  |  | 0.04951% | 99.38%
8 | 0.985 | -0.132 |  |  |  |  | 8 | 13800 | 13598 | 0.98536 | -0.2592 |  |  |  |  | 0.03678% | 96.36%
9 | 0.983 | -30.281 |  |  |  |  | 9 | 208 | 202.82 | 0.9751 | -31.0226 |  |  |  |  | 0.8041% | 2.449%
10 | 0.982 | -0.167 |  |  |  |  | 10 | 13800 | 13555.21 | 0.98226 | -0.2592 |  |  |  |  | 0.02664% | 55.21%
11 | 0.964 | -31.783 |  |  |  |  | 11 | 4160 | 4037.33 | 0.97051 | -31.3682 |  |  |  |  | 0.6755% | 1.305%
12 | 0.951 | -62.837 |  |  |  |  | 12 | 480 | 457.96 | 0.95408 | -62.7364 |  |  |  |  | 0.3242% | 0.1601%
13 | 0.954 | -62.593 |  |  |  |  | 13 | 480 | 459.97 | 0.95827 | -62.3908 |  |  |  |  | 0.4477% | 0.323%
14 | 0.963 | -31.794 |  |  |  |  | 14 | 4160 | 4033.56 | 0.96961 | -31.3682 |  |  |  |  | 0.686% | 1.339%
15 | 0.999 | 0.099 |  |  |  |  | 15 | 13800 | 13788.99 | 0.9992 | 0 |  |  |  |  | 0.02024% | -
16 | 1 | 0.315 | 1.5 | -1.09 |  |  | 16 | 13800 | 13801.45 | 1.0001 | 0.1728 | 1.5004 | -1.0084 |  |  | 0.01051% | 45.14% | 0.02667% | 7.486%
17 | 0.999 | 0.098 |  |  |  |  | 17 | 13800 | 13786.91 | 0.99905 | -0.086414 |  |  |  |  | 0.00515% | 188.2%
18 | 0.998 | -29.935 |  |  |  |  | 18 | 480 | 479.19 | 0.99831 | -30.072 |  |  |  |  | 0.03131% | 0.4577%
19 | 0.933 | -30.709 |  |  |  |  | 19 | 480 | 447.71 | 0.93273 | -30.8497 |  |  |  |  | 0.02903% | 0.4582%
|  |  | 4.09 | 1.8 | [7 empty] | 4.0957 | 1.7802 |  |  |  |  | 0.1394% | 1.1% | 4.4686 | 4.4659

## DiffOfPF - Fixed DG P
Case 1 = Matpower implementation with NO snubbers and NO measurement resistors. Typhoon Diesel Genset operates in PQ mode.
Case 2 = Matpower implementation with ALL snubbers and NO measurement resistors. Typhoon Diesel Genset operates in PQ mode.
Case 3 = Matpower implementation with NO snubbers and ALL measurement resistors. Typhoon Diesel Genset operates in PQ mode.
Case 4 = Matpower implementation with ALL snubbers and ALL measurement resistors. Typhoon Diesel Genset operates in PQ mode.
Single Case = Typhoon Case only. Typhoon Diesel Genset operates in PV mode. V = 1pu and P = 1.5MW.
This shows the difference caused by the snubbers, resistors for the measurements, and reactive power variation when calculating power flow with MATPOWER
Bus | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4
# | Vmag | Vmag | Vmag | Vmag | Vphase | Vphase | Vphase | Vphase | P | P | P | P | Q | Q | Q | Q
1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 2.55 | 2.55 | 2.59 | 2.59 | 3.09 | 2.9 | 3.08 | 2.89
2 | 0.998 | 0.998 | 0.998 | 0.998 | 0.023 | 0.019 | 0.022 | 0.018
3 | 0.996 | 0.996 | 0.996 | 0.996 | -0.004 | -0.008 | -0.005 | -0.009
4 | 0.993 | 0.994 | 0.993 | 0.994 | -30.185 | -30.189 | -30.186 | -30.19
5 | 0.985 | 0.985 | 0.985 | 0.985 | -30.85 | -30.854 | -30.852 | -30.855
6 | 0.952 | 0.952 | 0.952 | 0.952 | -31.25 | -31.254 | -31.252 | -31.255
7 | 0.985 | 0.985 | 0.985 | 0.985 | -0.103 | -0.127 | -0.106 | -0.13
8 | 0.985 | 0.985 | 0.985 | 0.985 | -0.105 | -0.128 | -0.108 | -0.132
9 | 0.983 | 0.983 | 0.983 | 0.983 | -30.254 | -30.278 | -30.257 | -30.281
10 | 0.981 | 0.982 | 0.981 | 0.982 | -0.134 | -0.164 | -0.137 | -0.167
11 | 0.964 | 0.964 | 0.964 | 0.964 | -31.749 | -31.779 | -31.753 | -31.783
12 | 0.951 | 0.951 | 0.951 | 0.951 | -62.803 | -62.833 | -62.807 | -62.837
13 | 0.954 | 0.954 | 0.954 | 0.954 | -62.559 | -62.59 | -62.563 | -62.593
14 | 0.963 | 0.963 | 0.963 | 0.963 | -31.76 | -31.79 | -31.764 | -31.794
15 | 0.999 | 0.999 | 0.999 | 0.999 | 0.105 | 0.1 | 0.104 | 0.099
16 | 1 | 1 | 1 | 1 | 0.318 | 0.317 | 0.315 | 0.315 | 1.5 | 1.5 | 1.5 | 1.5 | -0.98 | -1.1 | -0.97 | -1.09
17 | 0.999 | 0.999 | 0.999 | 0.999 | 0.104 | 0.1 | 0.103 | 0.098
18 | 0.998 | 0.998 | 0.998 | 0.998 | -29.929 | -29.934 | -29.931 | -29.935
19 | 0.933 | 0.933 | 0.932 | 0.933 | -30.703 | -30.707 | -30.704 | -30.709
This shows the difference caused by the variation of reactive power when measuring power flow with TYPHOON HIL
Bus | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4
# | Vmag | Vmag | Vmag | Vmag | Vphase | Vphase | Vphase | Vphase | P | P | P | P | Q | Q | Q | Q
1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 2.594 | 2.5938 | 2.5937 | 2.5936 | 2.8179 | 2.9092 | 2.7374 | 2.8791
2 | 0.99862 | 0.99859 | 0.99864 | 0.9986 | -0.0864 | -0.0864 | -0.0864 | -0.0864
3 | 0.99639 | 0.99637 | 0.99642 | 0.99638 | -0.1728 | -0.1728 | -0.1728 | -0.1728
4 | 0.9839 | 0.98388 | 0.98392 | 0.98389 | -31.0226 | -31.0226 | -31.0226 | -31.0226
5 | 0.98522 | 0.9852 | 0.98525 | 0.98521 | -30.9361 | -30.9361 | -30.9361 | -30.9361
6 | 0.95178 | 0.95176 | 0.9518 | 0.95177 | -31.3682 | -31.3682 | -31.3682 | -31.3682
7 | 0.98548 | 0.98546 | 0.9855 | 0.98546 | -0.2592 | -0.2592 | -0.2592 | -0.2592
8 | 0.98535 | 0.98533 | 0.98538 | 0.98534 | -0.2592 | -0.2592 | -0.2592 | -0.2592
9 | 0.9751 | 0.97507 | 0.97512 | 0.97508 | -31.0226 | -31.0226 | -31.0226 | -31.0226
10 | 0.98225 | 0.98223 | 0.98227 | 0.98224 | -0.2592 | -0.2592 | -0.2592 | -0.2592
11 | 0.9705 | 0.97048 | 0.97053 | 0.97049 | -31.3682 | -31.3682 | -31.3682 | -31.3682
12 | 0.95407 | 0.95405 | 0.95409 | 0.95406 | -62.7364 | -62.7364 | -62.7364 | -62.7364
13 | 0.95826 | 0.95824 | 0.95828 | 0.95825 | -62.3044 | -62.3044 | -62.3908 | -62.3044
14 | 0.9696 | 0.96957 | 0.96962 | 0.96958 | -31.3682 | -31.3682 | -31.3682 | -31.3682
15 | 0.99918 | 0.99911 | 0.99924 | 0.99913 | 0 | 0 | 0 | 0
16 | 1 | 0.9998 | 1.0002 | 0.99988 | 0.2016 | 0.2592 | 0.1728 | 0.2592 | 1.5004 | 1.5001 | 1.4996 | 1.5002 | -1.0406 | -1.1304 | -0.9595 | -1.1007
17 | 0.99903 | 0.99896 | 0.99909 | 0.99898 | -0.0864 | -0.0864 | -0.0864 | -0.0864
18 | 0.9983 | 0.99823 | 0.99836 | 0.99825 | -30.072 | -30.072 | -30.072 | -30.072
19 | 0.93271 | 0.93265 | 0.93277 | 0.93267 | -30.8497 | -30.8497 | -30.8497 | -30.8497
This shows the error between TYPHOON HIL and MATPOWER for each case
Bus | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4
# | Vmag | Vmag | Vmag | Vmag | Vphase | Vphase | Vphase | Vphase | P | P | P | P | Q | Q | Q | Q
1 | 0% | 0% | 0% | 0% | - | - | - | - | 1.725% | 1.718% | 0.1429% | 0.139% | 8.806% | 0.3172% | 11.12% | 0.3772% | The formatting of the cells help user to quickly see which value has the highest error. It's done as a color gradient that starts with the lowest value being green and ends with the highest value being red. The comparison includes the values of the same bus, under the same category , for each of the four cases. In other words, the comparison is only valid between columns. If a value is bigger than the average of the values compared, it is formatted in strong red with its font in bold and italic. If all values compared are equal, the cells are nof formatted.
2 | 0.06182% | 0.05947% | 0.06399% | 0.06027% | 475.7% | 554.7% | 492.7% | 580%
3 | 0.03961% | 0.03726% | 0.04178% | 0.03806% | 4220% | 2060% | 3356% | 1820%
4 | 0.9161% | 1.018% | 0.9139% | 1.017% | 2.775% | 2.761% | 2.771% | 2.758%
5 | 0.02269% | 0.02035% | 0.02487% | 0.02115% | 0.2791% | 0.2661% | 0.2726% | 0.2628%
6 | 0.02276% | 0.02512% | 0.02061% | 0.02431% | 0.3782% | 0.3654% | 0.3718% | 0.3622%
7 | 0.04869% | 0.04634% | 0.05086% | 0.04714% | 151.7% | 104.1% | 144.5% | 99.38%
8 | 0.03594% | 0.03359% | 0.03811% | 0.03439% | 146.9% | 102.5% | 140% | 96.36%
9 | 0.8039% | 0.8062% | 0.8017% | 0.8054% | 2.54% | 2.459% | 2.53% | 2.449%
10 | 0.1278% | 0.02346% | 0.1299% | 0.02426% | 93.43% | 58.05% | 89.2% | 55.21%
11 | 0.6747% | 0.6724% | 0.6769% | 0.6732% | 1.199% | 1.293% | 1.212% | 1.305%
12 | 0.3233% | 0.3209% | 0.3254% | 0.3217% | 0.106% | 0.1537% | 0.1124% | 0.1601%
13 | 0.4466% | 0.4443% | 0.4488% | 0.4451% | 0.407% | 0.4563% | 0.2752% | 0.4611%
14 | 0.6851% | 0.6827% | 0.6873% | 0.6835% | 1.234% | 1.327% | 1.246% | 1.339%
15 | 0.01789% | 0.01119% | 0.02407% | 0.01348% | - | - | - | -
16 | 0.002612% | 0.0196% | 0.02306% | 0.01204% | 36.6% | 18.23% | 45.14% | 17.71% | 0.02667% | 0.006667% | 0.02667% | 0.01333% | 6.184% | 2.764% | 1.082% | 0.9817%
17 | 0.002785% | 0.003902% | 0.008969% | 0.00162% | 183.1% | 186.4% | 183.9% | 188.2%
18 | 0.02968% | 0.02298% | 0.03586% | 0.02528% | 0.4778% | 0.461% | 0.4711% | 0.4577%
19 | 0.03086% | 0.03756% | 0.08257% | 0.03528% | 0.4778% | 0.4647% | 0.4745% | 0.4582%
Results below compare the 4 MATPOWER cases with TYPHOON single case where DG power is 1.5MW and control mode is PV
Typhoon single case - Diesel Genset in PV control mode. V = 1pu and P = 1.5MW
Bus | Case 1 |  |  |  | Case 1 |  |  |  | Case 1 |  |  |  | Case 1
# | Vmag |  |  |  | Vphase |  |  |  | P |  |  |  | Q
1 | 1 |  |  |  | 0 |  |  |  | 2.5953 |  |  |  | 2.7886
2 | 0.99863 |  |  |  | -0.0864
3 | 0.9964 |  |  |  | -0.1728
4 | 0.98408 |  |  |  | -31.0226
5 | 0.98523 |  |  |  | -30.9361
6 | 0.95179 |  |  |  | -31.3682
7 | 0.98549 |  |  |  | -0.2592
8 | 0.98536 |  |  |  | -0.2592
9 | 0.9751 |  |  |  | -31.0226
10 | 0.98226 |  |  |  | -0.2592
11 | 0.97051 |  |  |  | -31.3682
12 | 0.95408 |  |  |  | -62.7364
13 | 0.95827 |  |  |  | -62.3908
14 | 0.96961 |  |  |  | -31.3682
15 | 0.9992 |  |  |  | 0
16 | 1.0001 |  |  |  | 0.1728 |  |  |  | 1.5004 |  |  |  | -1.0084
17 | 0.99905 |  |  |  | -0.086414
18 | 0.99831 |  |  |  | -30.072
19 | 0.93273 |  |  |  | -30.8497
This shows the error between MATPOWER (each case) against TYPHOON (single case)
Bus | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4 | Case 1 | Case 2 | Case 3 | Case 4
# | Vmag | Vmag | Vmag | Vmag | Vphase | Vphase | Vphase | Vphase | P | P | P | P | Q | Q | Q | Q
1 | 0% | 0% | 0% | 0% | - | - | - | - | 1.776% | 1.776% | 0.2046% | 0.2046% | 9.754% | 3.841% | 9.461% | 3.509% | The formatting of the cells help user to quickly see which value has the highest error. It's done as a color gradient that starts with the lowest value being green and ends with the highest value being red. The comparison includes the values of the same bus, under the same category , for each of the four cases. In other words, the comparison is only valid between columns. If a value is bigger than the average of the values compared, it is formatted in strong red with its font in bold and italic. If all values compared are equal, the cells are nof formatted.
2 | 0.06266% | 0.06266% | 0.06266% | 0.06266% | 475.7% | 554.7% | 492.7% | 580%
3 | 0.04045% | 0.04045% | 0.04045% | 0.04045% | 4220% | 2060% | 3356% | 1820%
4 | 0.898% | 0.9977% | 0.898% | 0.9977% | 2.775% | 2.761% | 2.771% | 2.758%
5 | 0.02327% | 0.02327% | 0.02327% | 0.02327% | 0.2791% | 0.2661% | 0.2726% | 0.2628%
6 | 0.02188% | 0.02188% | 0.02188% | 0.02188% | 0.3782% | 0.3654% | 0.3718% | 0.3622%
7 | 0.04951% | 0.04951% | 0.04951% | 0.04951% | 151.7% | 104.1% | 144.5% | 99.38%
8 | 0.03678% | 0.03678% | 0.03678% | 0.03678% | 146.9% | 102.5% | 140% | 96.36%
9 | 0.8041% | 0.8041% | 0.8041% | 0.8041% | 2.54% | 2.459% | 2.53% | 2.449%
10 | 0.1286% | 0.02664% | 0.1286% | 0.02664% | 93.43% | 58.05% | 89.2% | 55.21%
11 | 0.6755% | 0.6755% | 0.6755% | 0.6755% | 1.199% | 1.293% | 1.212% | 1.305%
12 | 0.3242% | 0.3242% | 0.3242% | 0.3242% | 0.106% | 0.1537% | 0.1124% | 0.1601%
13 | 0.4477% | 0.4477% | 0.4477% | 0.4477% | 0.2689% | 0.3183% | 0.2752% | 0.323%
14 | 0.686% | 0.686% | 0.686% | 0.686% | 1.234% | 1.327% | 1.246% | 1.339%
15 | 0.02024% | 0.02024% | 0.02024% | 0.02024% | - | - | - | -
16 | 0.01051% | 0.01051% | 0.01051% | 0.01051% | 45.66% | 45.49% | 45.14% | 45.14% | 0.02667% | 0.02667% | 0.02667% | 0.02667% | 2.898% | 8.327% | 3.959% | 7.486%
17 | 0.00515% | 0.00515% | 0.00515% | 0.00515% | 183.1% | 186.4% | 183.9% | 188.2%
18 | 0.03131% | 0.03131% | 0.03131% | 0.03131% | 0.4778% | 0.461% | 0.4711% | 0.4577%
19 | 0.02903% | 0.02903% | 0.07824% | 0.02903% | 0.4778% | 0.4647% | 0.4745% | 0.4582%

## Data Collected - Various DG P
Case 1 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 0.0MW. DG operates in PV mode
Case 2 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 0.5MW. DG operates in PV mode
Case 3 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 1.0MW. DG operates in PV mode
Case 4 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 1.5MW. DG operates in PV mode
Case 5 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 2.0MW. DG operates in PV mode
Case 6 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 2.5MW. DG operates in PV mode
Case 7 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 3.0MW. DG operates in PV mode
Case 8 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 3.5MW. DG operates in PV mode
| Bus 1 is the SLACK bus - Stiff Grid | [6 empty] | Transmission lines are simple RL |  |  |  | Ts = 4e-6
| Bus 16 is the Diesel Genset Bus | [6 empty] | Voltage measurements are Line to Line
Case 1 - DG's P = 0.0MW
MATPOWER - No snubbers, No measurement resistors | [7 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [7 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) |  | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 4.08 | 1.8 |  |  |  | 1 | 13800 | 13800 | 1 | 0 | 4.0903 | 1.81 |  |  | 0% | - | 0.2525% | 0.5556% | 0%
2 | 0.998 | -0.026 | [5 empty] | 2 | 13800 | 13777.5049 | 0.99837 | -0.0864 |  |  |  |  | 0.03707% | 232.3% |  |  | -0.03707%
3 | 0.996 | -0.053 | [5 empty] | 3 | 13800 | 13746.876 | 0.99615 | -0.1728 |  |  |  |  | 0.0151% | 226% |  |  | -0.0151%
4 | 0.993 | -30.234 | [5 empty] | 4 | 480 | 472.1574 | 0.98366 | -31.0226 |  |  |  |  | 0.9405% | 2.608% |  |  | 0.9405%
5 | 0.985 | -30.9 | [5 empty] | 5 | 480 | 472.791 | 0.98498 | -31.0226 |  |  |  |  | 0.001904% | 0.3968% |  |  | 0.001904%
6 | 0.951 | -31.3 | [5 empty] | 6 | 480 | 456.7436 | 0.95155 | -31.3682 |  |  |  |  | 0.05775% | 0.2179% |  |  | -0.05775%
7 | 0.985 | -0.174 | [5 empty] | 7 | 13800 | 13595.1357 | 0.98515 | -0.2592 |  |  |  |  | 0.01571% | 48.97% |  |  | -0.01571%
8 | 0.985 | -0.176 | [5 empty] | 8 | 13800 | 13593.4033 | 0.98503 | -0.2592 |  |  |  |  | 0.002967% | 47.27% |  |  | -0.002967%
9 | 0.983 | -30.325 | [5 empty] | 9 | 208 | 202.7533 | 0.97478 | -31.0226 |  |  |  |  | 0.8367% | 2.3% |  |  | 0.8367% | Feeder1BansheeSimple.m
10 | 0.981 | -0.211 | [5 empty] | 10 | 13800 | 13550.3105 | 0.98191 | -0.3457 |  |  |  |  | 0.09241% | 63.84% |  |  | -0.09241%
11 | 0.964 | -31.827 |  |  |  |  | 4010.24 | 11 | 4160 | 4035.2346 | 0.97001 | -31.4546 |  |  |  |  | 0.6233% | 1.17% |  |  | -0.6233%
12 | 0.951 | -62.881 | [5 empty] | 12 | 480 | 457.7148 | 0.95357 | -62.7364 |  |  |  |  | 0.2705% | 0.23% |  |  | -0.2705%
13 | 0.954 | -62.638 | [5 empty] | 13 | 480 | 459.6778 | 0.95766 | -62.3908 |  |  |  |  | 0.3839% | 0.3946% |  |  | -0.3839%
14 | 0.963 | -31.838 | [5 empty] | 14 | 4160 | 4031.4651 | 0.9691 | -31.4546 |  |  |  |  | 0.6337% | 1.204% |  |  | -0.6337%
15 | 0.998 | -0.035 | [5 empty] | 15 | 13800 | 13778.123 | 0.99841 | -0.0864 |  |  |  |  | 0.04155% | 146.9% |  |  | -0.04155%
16 | 0.998 | -0.045 | 0 | 0 |  |  |  | 16 | 13800 | 13778.375 | 0.99843 | -0.1728 | 0 | 0 |  |  | 0.04338% | 284% | - | - | -0.04338%
17 | 0.998 | -0.036 | [5 empty] | 17 | 13800 | 13776.043 | 0.99826 | -0.1728 |  |  |  |  | 0.02645% | 380% |  |  | -0.02645%
18 | 0.997 | -30.069 | [5 empty] | 18 | 480 | 478.8144 | 0.99753 | -30.2448 |  |  |  |  | 0.05316% | 0.5847% |  |  | -0.05316%
19 | 0.932 | -30.843 | [5 empty] | 19 | 480 | 447.3582 | 0.932 | -30.9361 |  |  |  |  | 0.0004024% | 0.3019% |  |  | 0.0004024%
|  |  | 4.08 | 1.8 | [8 empty] | 4.0903 | 1.81 |  |  |  |  | 0.2525% | 0.5556%
Case 2 - DG's P = 0.5MW
MATPOWER - All Snubbers, No measurement resistors | [7 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [7 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) |  | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 3.58 | 1.57 |  |  |  | 1 | 13800 | 13800 | 1 | 0 | 3.5878 | 1.6528 |  |  | 0% | - | 0.2179% | 5.274%
2 | 0.998 | -0.023 | [5 empty] | 2 | 13800 | 13780.42 | 0.99858 | -0.0864 |  |  |  |  | 0.05823% | 275.7%
3 | 0.996 | -0.05 | [5 empty] | 3 | 13800 | 13749.75 | 0.99636 | -0.17283 |  |  |  |  | 0.03601% | 245.7%
4 | 0.994 | -30.231 | [5 empty] | 4 | 480 | 472.26 | 0.98387 | -31.0226 |  |  |  |  | 1.019% | 2.619%
5 | 0.985 | -30.897 | [5 empty] | 5 | 480 | 472.89 | 0.98519 | -31.0226 |  |  |  |  | 0.01904% | 0.4065%
6 | 0.952 | -31.297 | [5 empty] | 6 | 480 | 456.84 | 0.95175 | -31.3682 |  |  |  |  | 0.02626% | 0.2275%
7 | 0.985 | -0.171 | [5 empty] | 7 | 13800 | 13599.13 | 0.98544 | -0.2592 |  |  |  |  | 0.0451% | 51.58% |  |  |  | feeder1Banshee.m
8 | 0.985 | -0.173 | [5 empty] | 8 | 13800 | 13597.39 | 0.98532 | -0.2592 |  |  |  |  | 0.0323% | 49.83%
9 | 0.983 | -30.322 | [5 empty] | 9 | 208 | 202.81 | 0.97505 | -31.3682 |  |  |  |  | 0.8089% | 3.45%
10 | 0.982 | -0.208 | [5 empty] | 10 | 13800 | 13554.61 | 0.98222 | -0.3457 |  |  |  |  | 0.02221% | 66.2%
11 | 0.964 | -31.824 | [5 empty] | 11 | 4160 | 4037.15 | 0.97047 | -31.3682 |  |  |  |  | 0.671% | 1.432%
12 | 0.951 | -62.878 | [5 empty] | 12 | 480 | 457.94 | 0.95404 | -62.7364 |  |  |  |  | 0.3198% | 0.2252%
13 | 0.954 | -62.635 | [5 empty] | 13 | 480 | 459.95 | 0.95823 | -62.3908 |  |  |  |  | 0.4433% | 0.3899%
14 | 0.963 | -31.835 | [5 empty] | 14 | 4160 | 4033.38 | 0.96956 | -31.4546 |  |  |  |  | 0.6815% | 1.195%
15 | 0.999 | -0.026 | [5 empty] | 15 | 13800 | 13786.54 | 0.99902 | -0.0864 |  |  |  |  | 0.002466% | 232.3%
16 | 1 | -0.021 | 0.5 | 0.22 |  |  |  | 16 | 13800 | 13801.83 | 1.0001 | -0.0864 | 0.5004 | 0.1196 |  |  | 0.01326% | 311.4% | 0.08% | 45.64%
17 | 0.999 | -0.027 | [5 empty] | 17 | 13800 | 13784.46 | 0.99887 | -0.1728 |  |  |  |  | 0.01262% | 540%
18 | 0.998 | -30.06 | [5 empty] | 18 | 480 | 479.11 | 0.99815 | -30.2448 |  |  |  |  | 0.01461% | 0.6148%
19 | 0.933 | -30.834 | [5 empty] | 19 | 480 | 447.63 | 0.93256 | -30.9361 |  |  |  |  | 0.04689% | 0.3311%
|  |  | 4.08 | 1.79 | [8 empty] | 4.0882 | 1.7724 |  |  |  |  | 0.201% | 0.9832%
Case 3 - DG's P = 1.0MW
MATPOWER - No snubbers, All measurement resistors | [7 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [7 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) |  | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 3.09 | 2.23 |  |  |  | 1 | 13800 | 13800 | 1 | 0 | 3.0923 | 2.2173 |  |  | 0% | - | 0.07443% | 0.5695%
2 | 0.998 | -0.002 | [5 empty] | 2 | 13800 | 13780.75 | 0.99861 | -0.0864 |  |  |  |  | 0.06063% | 4220%
3 | 0.996 | -0.029 | [5 empty] | 3 | 13800 | 13750.08 | 0.99638 | -0.1728 |  |  |  |  | 0.03841% | 495.9%
4 | 0.994 | -30.211 | [5 empty] | 4 | 480 | 472.27 | 0.9839 | -30.76 |  |  |  |  | 1.017% | 1.817%
5 | 0.985 | -30.876 | [5 empty] | 5 | 480 | 472.9 | 0.98521 | -30.68 |  |  |  |  | 0.02115% | 0.6348%
6 | 0.952 | -31.276 | [5 empty] | 6 | 480 | 456.85 | 0.95177 | -31.11 |  |  |  |  | 0.02407% | 0.5308%
7 | 0.985 | -0.151 | [5 empty] | 7 | 13800 | 13599.46 | 0.98547 | -0.2592 |  |  |  |  | 0.04752% | 71.66% |  |  |  | feeder1BansheeNoSnubbers.m
8 | 0.985 | -0.152 | [5 empty] | 8 | 13800 | 13597.72 | 0.98534 | -0.2592 |  |  |  |  | 0.03472% | 70.53%
9 | 0.983 | -30.302 | [5 empty] | 9 | 208 | 202.82 | 0.9751 | -30.7633 |  |  |  |  | 0.8041% | 1.522%
10 | 0.982 | -0.187 | [5 empty] | 10 | 13800 | 13554.94 | 0.98224 | -0.3457 |  |  |  |  | 0.02465% | 84.87%
11 | 0.964 | -31.803 | [5 empty] | 11 | 4160 | 4037.25 | 0.97049 | -31.109 |  |  |  |  | 0.6735% | 2.182%
12 | 0.951 | -62.857 | [5 empty] | 12 | 480 | 457.95 | 0.95406 | -62.0451 |  |  |  |  | 0.322% | 1.292%
13 | 0.954 | -62.614 | [5 empty] | 13 | 480 | 459.96 | 0.95825 | -61.79 |  |  |  |  | 0.4455% | 1.316%
14 | 0.963 | -31.814 | [5 empty] | 14 | 4160 | 4033.48 | 0.96959 | -31.109 |  |  |  |  | 0.684% | 2.216%
15 | 0.999 | 0.037 | [5 empty] | 15 | 13800 | 13787.85 | 0.99912 | 0 |  |  |  |  | 0.01197% | -
16 | 1 | 0.147 | 1 | -0.43 |  |  |  | 16 | 13800 | 13801.85 | 1.0001 | 0.0864 | 0.9998 | -0.4409 |  |  | 0.01341% | 41.22% | 0.02% | 2.535%
17 | 0.999 | 0.036 | [5 empty] | 17 | 13800 | 13785.76 | 0.99897 | -0.0864 |  |  |  |  | 0.003192% | 340%
18 | 0.998 | -29.997 | [5 empty] | 18 | 480 | 479.15 | 0.99823 | -30.16 |  |  |  |  | 0.02296% | 0.5434%
19 | 0.933 | -30.771 | [5 empty] | 19 | 480 | 447.68 | 0.93267 | -30.85 |  |  |  |  | 0.03573% | 0.2567%
|  |  | 4.09 | 1.8 | [8 empty] | 4.0921 | 1.7764 |  |  |  |  | 0.05134% | 1.311%
Case 4 - DG's P = 1.5MW
MATPOWER - ALL snubbers, All measurement resistors | [7 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [7 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) |  | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.59 | 2.89 |  |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.5953 | 2.7886 |  |  | 0% | - | 0.2046% | 3.509%
2 | 0.998 | 0.018 | [5 empty] | 2 | 13800 | 13781.03 | 0.99863 | -0.0864 |  |  |  |  | 0.06266% | 580%
3 | 0.996 | -0.009 | [5 empty] | 3 | 13800 | 13750.36 | 0.9964 | -0.1728 |  |  |  |  | 0.04045% | 1820%
4 | 0.994 | -30.19 |  |  |  |  | 476.64 | 4 | 480 | 472.36 | 0.98408 | -31.0226 |  |  |  |  | 0.9977% | 2.758%
5 | 0.985 | -30.855 | [5 empty] | 5 | 480 | 472.91 | 0.98523 | -30.9361 |  |  |  |  | 0.02327% | 0.2628%
6 | 0.952 | -31.255 | [5 empty] | 6 | 480 | 456.86 | 0.95179 | -31.3682 |  |  |  |  | 0.02188% | 0.3622%
7 | 0.985 | -0.13 | [5 empty] | 7 | 13800 | 13599.73 | 0.98549 | -0.2592 |  |  |  |  | 0.04951% | 99.38%
8 | 0.985 | -0.132 | [5 empty] | 8 | 13800 | 13598 | 0.98536 | -0.2592 |  |  |  |  | 0.03678% | 96.36%
9 | 0.983 | -30.281 | [5 empty] | 9 | 208 | 202.82 | 0.9751 | -31.0226 |  |  |  |  | 0.8041% | 2.449% |  |  |  | Feeder1BansheeFULL.m
10 | 0.982 | -0.167 | [5 empty] | 10 | 13800 | 13555.21 | 0.98226 | -0.2592 |  |  |  |  | 0.02664% | 55.21%
11 | 0.964 | -31.783 | [5 empty] | 11 | 4160 | 4037.33 | 0.97051 | -31.3682 |  |  |  |  | 0.6755% | 1.305%
12 | 0.951 | -62.837 | [5 empty] | 12 | 480 | 457.96 | 0.95408 | -62.7364 |  |  |  |  | 0.3242% | 0.1601%
13 | 0.954 | -62.593 | [5 empty] | 13 | 480 | 459.97 | 0.95827 | -62.3908 |  |  |  |  | 0.4477% | 0.323%
14 | 0.963 | -31.794 | [5 empty] | 14 | 4160 | 4033.56 | 0.96961 | -31.3682 |  |  |  |  | 0.686% | 1.339%
15 | 0.999 | 0.099 | [5 empty] | 15 | 13800 | 13788.99 | 0.9992 | 0 |  |  |  |  | 0.02024% | -
16 | 1 | 0.315 | 1.5 | -1.09 |  |  |  | 16 | 13800 | 13801.45 | 1.0001 | 0.1728 | 1.5004 | -1.0084 |  |  | 0.01051% | 45.14% | 0.02667% | 7.486%
17 | 0.999 | 0.098 | [5 empty] | 17 | 13800 | 13786.91 | 0.99905 | -0.086414 |  |  |  |  | 0.00515% | 188.2%
18 | 0.998 | -29.935 | [5 empty] | 18 | 480 | 479.19 | 0.99831 | -30.072 |  |  |  |  | 0.03131% | 0.4577%
19 | 0.933 | -30.709 | [5 empty] | 19 | 480 | 447.71 | 0.93273 | -30.8497 |  |  |  |  | 0.02903% | 0.4582%
|  |  | 4.09 | 1.8 | [8 empty] | 4.0957 | 1.7802 |  |  |  |  | 0.1394% | 1.1%
Case 5 - DG's P = 2.0MW
MATPOWER - ALL snubbers, All measurement resistors | [7 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [7 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) |  | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.1 | 3.55 |  |  |  | 1 | 13800 | 13800 | 1 | 0 | 2.1001 | 3.339 |  |  | 0% | - | 0.004762% | 5.944%
2 | 0.998 | 0.039 | [5 empty] | 2 | 13800 | 13781.38 | 0.99865 | -0.0864 |  |  |  |  | 0.0652% | 321.5%
3 | 0.996 | 0.012 | [5 empty] | 3 | 13800 | 13750.71 | 0.99643 | -0.1728 |  |  |  |  | 0.043% | 1540%
4 | 0.993 | -30.169 | [5 empty] | 4 | 480 | 472.29 | 0.98394 | -31.0226 |  |  |  |  | 0.9126% | 2.829%
5 | 0.985 | -30.835 | [5 empty] | 5 | 480 | 472.92 | 0.98525 | -30.9361 |  |  |  |  | 0.02538% | 0.3279%
6 | 0.952 | -31.235 | [5 empty] | 6 | 480 | 456.87 | 0.95181 | -31.3682 |  |  |  |  | 0.0197% | 0.4264%
7 | 0.985 | -0.109 | [5 empty] | 7 | 13800 | 13600.08 | 0.98551 | -0.2592 |  |  |  |  | 0.05209% | 137.8%
8 | 0.985 | -0.111 | [5 empty] | 8 | 13800 | 13598.34 | 0.98539 | -0.2592 |  |  |  |  | 0.03928% | 133.5%
9 | 0.983 | -30.26 | [5 empty] | 9 | 208 | 202.83 | 0.97514 | -30.9361 |  |  |  |  | 0.7992% | 2.234%
10 | 0.982 | -0.146 | [5 empty] | 10 | 13800 | 13555.55 | 0.98229 | -0.2592 |  |  |  |  | 0.02915% | 77.53%
11 | 0.964 | -31.762 | [5 empty] | 11 | 4160 | 4037.43 | 0.97054 | -31.3682 |  |  |  |  | 0.678% | 1.24%
12 | 0.951 | -62.816 | [5 empty] | 12 | 480 | 457.97 | 0.9541 | -62.7364 |  |  |  |  | 0.3264% | 0.1267%
13 | 0.954 | -62.573 | [5 empty] | 13 | 480 | 459.98 | 0.95829 | -62.3044 |  |  |  |  | 0.4499% | 0.4293%
14 | 0.963 | -31.773 | [5 empty] | 14 | 4160 | 4033.66 | 0.96963 | -31.3682 |  |  |  |  | 0.6885% | 1.274%
15 | 0.999 | 0.161 | [5 empty] | 15 | 13800 | 13790.35 | 0.9993 | 0.0864 |  |  |  |  | 0.0301% | 46.34%
16 | 1 | 0.482 | 2 | -1.74 |  |  |  | 16 | 13800 | 13801.82 | 1.0001 | 0.3457 | 2.0001 | -1.5546 |  |  | 0.01319% | 28.28% | 0.005% | 10.66%
17 | 0.999 | 0.16 | [5 empty] | 17 | 13800 | 13788.27 | 0.99915 | 0 |  |  |  |  | 0.01502% | -
18 | 0.998 | -29.873 | [5 empty] | 18 | 480 | 479.24 | 0.99842 | -30.072 |  |  |  |  | 0.04175% | 0.6662%
19 | 0.933 | -30.647 | [5 empty] | 19 | 480 | 447.76 | 0.93283 | -30.7633 |  |  |  |  | 0.01786% | 0.3795%
|  |  | 4.1 | 1.81 | [8 empty] | 4.1002 | 1.7844 |  |  |  |  | 0.004878% | 1.414%
Case 6 - DG's P = 2.5MW
MATPOWER - ALL snubbers, All measurement resistors | [7 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [7 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) |  | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 1.61 | 4.21 |  |  |  | 1 | 13800 | 13800 | 1 | 0 | 1.6101 | 3.904 |  |  | 0% | - | 0.006211% | 7.268%
2 | 0.998 | 0.059 | [5 empty] | 2 | 13800 | 13781.68 | 0.99867 | 0 |  |  |  |  | 0.06738% | -
3 | 0.996 | 0.032 | [5 empty] | 3 | 13800 | 13751.01 | 0.99645 | -0.0864 |  |  |  |  | 0.04518% | 370%
4 | 0.993 | -30.149 | [5 empty] | 4 | 480 | 472.3 | 0.98396 | -30.9361 |  |  |  |  | 0.9105% | 2.611%
5 | 0.985 | -30.814 | [5 empty] | 5 | 480 | 472.93 | 0.98527 | -30.9361 |  |  |  |  | 0.0275% | 0.3962%
6 | 0.952 | -31.214 | [5 empty] | 6 | 480 | 456.88 | 0.95183 | -31.2818 |  |  |  |  | 0.01751% | 0.2172%
7 | 0.985 | -0.089 | [5 empty] | 7 | 13800 | 13600.37 | 0.98553 | -0.2592 |  |  |  |  | 0.05422% | 191.2%
8 | 0.985 | -0.09 | [5 empty] | 8 | 13800 | 13598.64 | 0.98541 | -0.2592 |  |  |  |  | 0.04149% | 188%
9 | 0.983 | -30.24 | [5 empty] | 9 | 208 | 202.83 | 0.97514 | -30.9361 |  |  |  |  | 0.7992% | 2.302%
10 | 0.982 | -0.126 | [5 empty] | 10 | 13800 | 13555.85 | 0.98231 | -0.2592 |  |  |  |  | 0.03136% | 105.7%
11 | 0.964 | -31.741 | [5 empty] | 11 | 4160 | 4037.52 | 0.97056 | -31.3682 |  |  |  |  | 0.6803% | 1.175%
12 | 0.951 | -62.796 | [5 empty] | 12 | 480 | 457.98 | 0.95413 | -62.7364 |  |  |  |  | 0.3286% | 0.09491%
13 | 0.954 | -62.552 | [5 empty] | 13 | 480 | 459.99 | 0.95831 | -62.3044 |  |  |  |  | 0.452% | 0.3958%
14 | 0.963 | -31.753 | [5 empty] | 14 | 4160 | 4033.75 | 0.96965 | -31.3682 |  |  |  |  | 0.6907% | 1.212%
15 | 0.999 | 0.223 | [5 empty] | 15 | 13800 | 13791.58 | 0.99939 | 0.0864 |  |  |  |  | 0.03902% | 61.26%
16 | 1 | 0.649 | 2.5 | -2.39 |  |  |  | 16 | 13800 | 13801.84 | 1.0001 | 0.5185 | 2.5008 | -2.1093 |  |  | 0.01333% | 20.11% | 0.032% | 11.74%
17 | 0.999 | 0.221 | [5 empty] | 17 | 13800 | 13789.49 | 0.99924 | 0 |  |  |  |  | 0.02386% | -
18 | 0.998 | -29.812 | [5 empty] | 18 | 480 | 479.28 | 0.9985 | -29.9856 |  |  |  |  | 0.0501% | 0.5823%
19 | 0.933 | -30.586 | [5 empty] | 19 | 480 | 447.8 | 0.93292 | -30.7633 |  |  |  |  | 0.008932% | 0.5797%
|  |  | 4.11 | 1.82 | [8 empty] | 4.1109 | 1.7947 |  |  |  |  | 0.0219% | 1.39%
Case 7 - DG's P = 3.0MW
MATPOWER - ALL snubbers, All measurement resistors | [7 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [7 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) |  | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 1.13 | 4.87 |  |  |  | 1 | 13800 | 13800 | 1 | 0 | 1.1212 | 4.4611 |  |  | 0% | - | 0.7788% | 8.396%
2 | 0.998 | 0.08 | [5 empty] | 2 | 13800 | 13781.96 | 0.99869 | 0 |  |  |  |  | 0.06941% | -
3 | 0.996 | 0.053 | [5 empty] | 3 | 13800 | 13751.29 | 0.99647 | -0.0864 |  |  |  |  | 0.04722% | 263%
4 | 0.993 | -30.129 | [5 empty] | 4 | 480 | 472.31 | 0.98398 | -30.9361 |  |  |  |  | 0.9084% | 2.679%
5 | 0.985 | -30.794 | [5 empty] | 5 | 480 | 472.94 | 0.98529 | -30.9361 |  |  |  |  | 0.02961% | 0.4615%
6 | 0.952 | -31.194 | [5 empty] | 6 | 480 | 456.89 | 0.95185 | -31.2818 |  |  |  |  | 0.01532% | 0.2815%
7 | 0.985 | -0.069 | [5 empty] | 7 | 13800 | 13600.66 | 0.98556 | -0.1728 |  |  |  |  | 0.05635% | 150.4%
8 | 0.985 | -0.07 | [5 empty] | 8 | 13800 | 13598.92 | 0.98543 | -0.1728 |  |  |  |  | 0.04355% | 146.9%
9 | 0.983 | -30.219 | [5 empty] | 9 | 208 | 202.84 | 0.97519 | -30.9361 |  |  |  |  | 0.7943% | 2.373%
10 | 0.982 | -0.105 | [5 empty] | 10 | 13800 | 13556.13 | 0.98233 | -0.2592 |  |  |  |  | 0.03343% | 146.9%
11 | 0.964 | -31.721 | [5 empty] | 11 | 4160 | 4037.61 | 0.97058 | -31.2818 |  |  |  |  | 0.6825% | 1.385%
12 | 0.951 | -62.775 | [5 empty] | 12 | 480 | 457.99 | 0.95415 | -62.65 |  |  |  |  | 0.3308% | 0.1991%
13 | 0.954 | -62.532 | [5 empty] | 13 | 480 | 460 | 0.95833 | -62.3 |  |  |  |  | 0.4542% | 0.371%
14 | 0.963 | -31.732 | [5 empty] | 14 | 4160 | 4033.84 | 0.96967 | -31.28 |  |  |  |  | 0.6929% | 1.424%
15 | 0.999 | 0.284 | [5 empty] | 15 | 13800 | 13792.76 | 0.99948 | 0.1728 |  |  |  |  | 0.04758% | -
16 | 1 | 0.815 | 3 | -3.04 |  |  |  | 16 | 13800 | 13801.86 | 1.0001 | 0.6913 | 3.0002 | -2.6576 |  |  | 0.01348% | 15.18% | 0.006667% | 12.58%
17 | 0.999 | 0.283 | [5 empty] | 17 | 13800 | 13790.68 | 0.99932 | 0.0864 |  |  |  |  | 0.0325% | 69.47%
18 | 0.998 | -29.75 | [5 empty] | 18 | 480 | 479.33 | 0.9986 | -29.99 |  |  |  |  | 0.06054% | 0.8067%
19 | 0.933 | -30.524 | [5 empty] | 19 | 480 | 447.84 | 0.933 | -30.68 |  |  |  |  | 1.19e-14% | 0.5111%
|  |  | 4.13 | 1.83 | [8 empty] | 4.1214 | 1.8035 |  |  |  |  | 0.2082% | 1.448%
Case 8 - DG's P = 3.5MW
MATPOWER - ALL snubbers, All measurement resistors | [7 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [7 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) |  | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 0.65 | 5.53 |  |  |  | 1 | 13800 | 13800 | 1 | 0 | 0.6387 | 5.0107 |  |  | 0% | - | 1.738% | 9.391%
2 | 0.998 | 0.1 | [5 empty] | 2 | 13800 | 13782.2363 | 0.99871 | 0 |  |  |  |  | 0.07142% | -
3 | 0.996 | 0.073 | [5 empty] | 3 | 13800 | 13751.5635 | 0.99649 | -0.0864 |  |  |  |  | 0.04921% | 218.4%
4 | 0.993 | -30.108 | [5 empty] | 4 | 480 | 472.3193 | 0.984 | -30.9361 |  |  |  |  | 0.9065% | 2.75%
5 | 0.985 | -30.774 | [5 empty] | 5 | 480 | 472.9532 | 0.98532 | -30.8497 |  |  |  |  | 0.0324% | 0.246%
6 | 0.952 | -31.174 | [5 empty] | 6 | 480 | 456.9003 | 0.95188 | -31.2818 |  |  |  |  | 0.01306% | 0.3458%
7 | 0.985 | -0.048 | [5 empty] | 7 | 13800 | 13600.9229 | 0.98557 | -0.1728 |  |  |  |  | 0.05829% | 260%
8 | 0.985 | -0.05 | [5 empty] | 8 | 13800 | 13599.1895 | 0.98545 | -0.1728 |  |  |  |  | 0.04553% | 245.6%
9 | 0.983 | -30.199 | [5 empty] | 9 | 208 | 202.8401 | 0.97519 | -30.9361 |  |  |  |  | 0.7942% | 2.441%
10 | 0.982 | -0.085 | [5 empty] | 10 | 13800 | 13556.3975 | 0.98235 | -0.1728 |  |  |  |  | 0.0354% | 103.3%
11 | 0.964 | -31.701 | [5 empty] | 11 | 4160 | 4037.6892 | 0.9706 | -31.2818 |  |  |  |  | 0.6845% | 1.322%
12 | 0.951 | -62.755 | [5 empty] | 12 | 480 | 458.0003 | 0.95417 | -62.65 |  |  |  |  | 0.333% | 0.1673%
13 | 0.954 | -62.512 | [5 empty] | 13 | 480 | 460.0101 | 0.95835 | -62.3044 |  |  |  |  | 0.4564% | 0.3321%
14 | 0.963 | -31.712 | [5 empty] | 14 | 4160 | 4033.9167 | 0.96969 | -31.2818 |  |  |  |  | 0.6949% | 1.357%
15 | 0.999 | 0.345 | [5 empty] | 15 | 13800 | 13793.9189 | 0.99956 | 0.2592 |  |  |  |  | 0.05599% | -
16 | 1 | 0.98 | 3.5 | -3.68 |  |  |  | 16 | 13800 | 13801.8438 | 1.0001 | 0.8641 | 3.5003 | -3.1937 |  |  | 0.01336% | 11.83% | 0.008571% | 13.21%
17 | 0.999 | 0.344 | [5 empty] | 17 | 13800 | 13791.8359 | 0.99941 | 0.1728 |  |  |  |  | 0.04088% | 49.77%
18 | 0.998 | -29.689 | [5 empty] | 18 | 480 | 479.3662 | 0.99868 | -29.8992 |  |  |  |  | 0.06809% | 0.708%
19 | 0.932 | -30.463 | [5 empty] | 19 | 480 | 447.8737 | 0.93307 | -30.5905 |  |  |  |  | 0.1148% | 0.4185%
|  |  | 4.15 | 1.85 | [8 empty] | 4.139 | 1.817 |  |  |  |  | 0.2651% | 1.784%

## DiffOfPF - Various DG P
Case 1 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 0.0MW. DG operates in PV mode
Case 2 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 0.5MW. DG operates in PV mode
Case 3 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 1.0MW. DG operates in PV mode
Case 4 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 1.5MW. DG operates in PV mode
Case 5 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 2.0MW. DG operates in PV mode
Case 6 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 2.5MW. DG operates in PV mode
Case 7 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 3.0MW. DG operates in PV mode
Case 8 = Matpower implementation with ALL snubbers and ALL measurement resistors. Both implementations have DG P = 3.5MW. DG operates in PV mode
This shows the different results of MATPOWER when changing the genset active power output
Bus | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8
# | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | P | P | P | P | P | P | P | P | Q | Q | Q | Q | Q | Q | Q | Q
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.08 | 3.58 | 3.09 | 2.59 | 2.1 | 1.61 | 1.13 | 0.65 | 1.8 | 1.57 | 2.23 | 2.89 | 3.55 | 4.21 | 4.87 | 5.53
2 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | -0.026 | -0.023 | -0.002 | 0.018 | 0.039 | 0.059 | 0.08 | 0.1
3 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | -0.053 | -0.05 | -0.029 | -0.009 | 0.012 | 0.032 | 0.053 | 0.073
4 | 0.993 | 0.994 | 0.994 | 0.994 | 0.993 | 0.993 | 0.993 | 0.993 | -30.234 | -30.231 | -30.211 | -30.19 | -30.169 | -30.149 | -30.129 | -30.108
5 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | -30.9 | -30.897 | -30.876 | -30.855 | -30.835 | -30.814 | -30.794 | -30.774
6 | 0.951 | 0.952 | 0.952 | 0.952 | 0.952 | 0.952 | 0.952 | 0.952 | -31.3 | -31.297 | -31.276 | -31.255 | -31.235 | -31.214 | -31.194 | -31.174
7 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | -0.174 | -0.171 | -0.151 | -0.13 | -0.109 | -0.089 | -0.069 | -0.048
8 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | -0.176 | -0.173 | -0.152 | -0.132 | -0.111 | -0.09 | -0.07 | -0.05
9 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | -30.325 | -30.322 | -30.302 | -30.281 | -30.26 | -30.24 | -30.219 | -30.199
10 | 0.981 | 0.982 | 0.982 | 0.982 | 0.982 | 0.982 | 0.982 | 0.982 | -0.211 | -0.208 | -0.187 | -0.167 | -0.146 | -0.126 | -0.105 | -0.085
11 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | -31.827 | -31.824 | -31.803 | -31.783 | -31.762 | -31.741 | -31.721 | -31.701
12 | 0.951 | 0.951 | 0.951 | 0.951 | 0.951 | 0.951 | 0.951 | 0.951 | -62.881 | -62.878 | -62.857 | -62.837 | -62.816 | -62.796 | -62.775 | -62.755
13 | 0.954 | 0.954 | 0.954 | 0.954 | 0.954 | 0.954 | 0.954 | 0.954 | -62.638 | -62.635 | -62.614 | -62.593 | -62.573 | -62.552 | -62.532 | -62.512
14 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | 0.963 | -31.838 | -31.835 | -31.814 | -31.794 | -31.773 | -31.753 | -31.732 | -31.712
15 | 0.998 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | -0.035 | -0.026 | 0.037 | 0.099 | 0.161 | 0.223 | 0.284 | 0.345
16 | 0.998 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | -0.045 | -0.021 | 0.147 | 0.315 | 0.482 | 0.649 | 0.815 | 0.98 | 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 0 | 0.22 | -0.43 | -1.09 | -1.74 | -2.39 | -3.04 | -3.68
17 | 0.998 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | -0.036 | -0.027 | 0.036 | 0.098 | 0.16 | 0.221 | 0.283 | 0.344
18 | 0.997 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | -30.069 | -30.06 | -29.997 | -29.935 | -29.873 | -29.812 | -29.75 | -29.689
19 | 0.932 | 0.933 | 0.933 | 0.933 | 0.933 | 0.933 | 0.933 | 0.932 | -30.843 | -30.834 | -30.771 | -30.709 | -30.647 | -30.586 | -30.524 | -30.463
This shows the different results of TYPHOON HIL when changing the genset active power output
Bus | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8
# | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | P | P | P | P | P | P | P | P | Q | Q | Q | Q | Q | Q | Q | Q
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0903 | 3.5878 | 3.0923 | 2.5953 | 2.1001 | 1.6101 | 1.1212 | 0.6387 | 1.81 | 1.6528 | 2.2173 | 2.7886 | 3.339 | 3.904 | 4.4611 | 5.0107
2 | 0.99837 | 0.99858 | 0.99861 | 0.99863 | 0.99865 | 0.99867 | 0.99869 | 0.99871 | -0.0864 | -0.0864 | -0.0864 | -0.0864 | -0.0864 | 0 | 0 | 0
3 | 0.99615 | 0.99636 | 0.99638 | 0.9964 | 0.99643 | 0.99645 | 0.99647 | 0.99649 | -0.1728 | -0.17283 | -0.1728 | -0.1728 | -0.1728 | -0.0864 | -0.0864 | -0.0864
4 | 0.98366 | 0.98387 | 0.9839 | 0.98408 | 0.98394 | 0.98396 | 0.98398 | 0.984 | -31.0226 | -31.0226 | -30.76 | -31.0226 | -31.0226 | -30.9361 | -30.9361 | -30.9361
5 | 0.98498 | 0.98519 | 0.98521 | 0.98523 | 0.98525 | 0.98527 | 0.98529 | 0.98532 | -31.0226 | -31.0226 | -30.68 | -30.9361 | -30.9361 | -30.9361 | -30.9361 | -30.8497
6 | 0.95155 | 0.95175 | 0.95177 | 0.95179 | 0.95181 | 0.95183 | 0.95185 | 0.95188 | -31.3682 | -31.3682 | -31.11 | -31.3682 | -31.3682 | -31.2818 | -31.2818 | -31.2818
7 | 0.98515 | 0.98544 | 0.98547 | 0.98549 | 0.98551 | 0.98553 | 0.98556 | 0.98557 | -0.2592 | -0.2592 | -0.2592 | -0.2592 | -0.2592 | -0.2592 | -0.1728 | -0.1728
8 | 0.98503 | 0.98532 | 0.98534 | 0.98536 | 0.98539 | 0.98541 | 0.98543 | 0.98545 | -0.2592 | -0.2592 | -0.2592 | -0.2592 | -0.2592 | -0.2592 | -0.1728 | -0.1728
9 | 0.97478 | 0.97505 | 0.9751 | 0.9751 | 0.97514 | 0.97514 | 0.97519 | 0.97519 | -31.0226 | -31.3682 | -30.7633 | -31.0226 | -30.9361 | -30.9361 | -30.9361 | -30.9361
10 | 0.98191 | 0.98222 | 0.98224 | 0.98226 | 0.98229 | 0.98231 | 0.98233 | 0.98235 | -0.3457 | -0.3457 | -0.3457 | -0.2592 | -0.2592 | -0.2592 | -0.2592 | -0.1728
11 | 0.97001 | 0.97047 | 0.97049 | 0.97051 | 0.97054 | 0.97056 | 0.97058 | 0.9706 | -31.4546 | -31.3682 | -31.109 | -31.3682 | -31.3682 | -31.3682 | -31.2818 | -31.2818
12 | 0.95357 | 0.95404 | 0.95406 | 0.95408 | 0.9541 | 0.95413 | 0.95415 | 0.95417 | -62.7364 | -62.7364 | -62.0451 | -62.7364 | -62.7364 | -62.7364 | -62.65 | -62.65
13 | 0.95766 | 0.95823 | 0.95825 | 0.95827 | 0.95829 | 0.95831 | 0.95833 | 0.95835 | -62.3908 | -62.3908 | -61.79 | -62.3908 | -62.3044 | -62.3044 | -62.3 | -62.3044
14 | 0.9691 | 0.96956 | 0.96959 | 0.96961 | 0.96963 | 0.96965 | 0.96967 | 0.96969 | -31.4546 | -31.4546 | -31.109 | -31.3682 | -31.3682 | -31.3682 | -31.28 | -31.2818
15 | 0.99841 | 0.99902 | 0.99912 | 0.9992 | 0.9993 | 0.99939 | 0.99948 | 0.99956 | -0.0864 | -0.0864 | 0 | 0 | 0.0864 | 0.0864 | 0.1728 | 0.2592
16 | 0.99843 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | -0.1728 | -0.0864 | 0.0864 | 0.1728 | 0.3457 | 0.5185 | 0.6913 | 0.8641 | 0 | 0.5004 | 0.9998 | 1.5004 | 2.0001 | 2.5008 | 3.0002 | 3.5003 | 0 | 0.1196 | -0.4409 | -1.0084 | -1.5546 | -2.1093 | -2.6576 | -3.1937
17 | 0.99826 | 0.99887 | 0.99897 | 0.99905 | 0.99915 | 0.99924 | 0.99932 | 0.99941 | -0.1728 | -0.1728 | -0.0864 | -0.086414 | 0 | 0 | 0.0864 | 0.1728
18 | 0.99753 | 0.99815 | 0.99823 | 0.99831 | 0.99842 | 0.9985 | 0.9986 | 0.99868 | -30.2448 | -30.2448 | -30.16 | -30.072 | -30.072 | -29.9856 | -29.99 | -29.8992
19 | 0.932 | 0.93256 | 0.93267 | 0.93273 | 0.93283 | 0.93292 | 0.933 | 0.93307 | -30.9361 | -30.9361 | -30.85 | -30.8497 | -30.7633 | -30.7633 | -30.68 | -30.5905
This shows the error between TYPHOON HIL and MATPOWER for each case
Bus | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8
# | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vmag | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | Vphase | P | P | P | P | P | P | P | P | Q | Q | Q | Q | Q | Q | Q | Q
[9 empty] | - | - | - | - | - | - | - | - | 0.2525% | 0.2179% | 0.07443% | 0.2046% | 0.004762% | 0.006211% | 0.7788% | 1.738% | 0.5556% | 5.274% | 0.5695% | 3.509% | 5.944% | 7.268% | 8.396% | 9.391% | bar: 13 to 0.95835
2 | 0.03707% | 0.05823% | 0.06063% | 0.06266% | 0.0652% | 0.06738% | 0.06941% | 0.07142% | 232.3% | 275.7% | 4220% | 580% | 321.5% | - | - | -
3 | 0.0151% | 0.03601% | 0.03841% | 0.04045% | 0.043% | 0.04518% | 0.04722% | 0.04921% | 226% | 245.7% | 495.9% | 1820% | 1540% | 370% | 263% | 218.4%
4 | 0.9405% | 1.019% | 1.017% | 0.9977% | 0.9126% | 0.9105% | 0.9084% | 0.9065% | 2.608% | 2.619% | 1.817% | 2.758% | 2.829% | 2.611% | 2.679% | 2.75%
5 | 0.001904% | 0.01904% | 0.02115% | 0.02327% | 0.02538% | 0.0275% | 0.02961% | 0.0324% | 0.3968% | 0.4065% | 0.6348% | 0.2628% | 0.3279% | 0.3962% | 0.4615% | 0.246%
6 | 0.05775% | 0.02626% | 0.02407% | 0.02188% | 0.0197% | 0.01751% | 0.01532% | 0.01306% | 0.2179% | 0.2275% | 0.5308% | 0.3622% | 0.4264% | 0.2172% | 0.2815% | 0.3458%
7 | 0.01571% | 0.0451% | 0.04752% | 0.04951% | 0.05209% | 0.05422% | 0.05635% | 0.05829% | 48.97% | 51.58% | 71.66% | 99.38% | 137.8% | 191.2% | 150.4% | 260%
8 | 0.002967% | 0.0323% | 0.03472% | 0.03678% | 0.03928% | 0.04149% | 0.04355% | 0.04553% | 47.27% | 49.83% | 70.53% | 96.36% | 133.5% | 188% | 146.9% | 245.6%
9 | 0.8367% | 0.8089% | 0.8041% | 0.8041% | 0.7992% | 0.7992% | 0.7943% | 0.7942% | 2.3% | 3.45% | 1.522% | 2.449% | 2.234% | 2.302% | 2.373% | 2.441%
10 | 0.09241% | 0.02221% | 0.02465% | 0.02664% | 0.02915% | 0.03136% | 0.03343% | 0.0354% | 63.84% | 66.2% | 84.87% | 55.21% | 77.53% | 105.7% | 146.9% | 103.3%
11 | 0.6233% | 0.671% | 0.6735% | 0.6755% | 0.678% | 0.6803% | 0.6825% | 0.6845% | 1.17% | 1.432% | 2.182% | 1.305% | 1.24% | 1.175% | 1.385% | 1.322%
12 | 0.2705% | 0.3198% | 0.322% | 0.3242% | 0.3264% | 0.3286% | 0.3308% | 0.333% | 0.23% | 0.2252% | 1.292% | 0.1601% | 0.1267% | 0.09491% | 0.1991% | 0.1673%
13 | 0.3839% | 0.4433% | 0.4455% | 0.4477% | 0.4499% | 0.452% | 0.4542% | 0.4564% | 0.3946% | 0.3899% | 1.316% | 0.323% | 0.4293% | 0.3958% | 0.371% | 0.3321%
14 | 0.6337% | 0.6815% | 0.684% | 0.686% | 0.6885% | 0.6907% | 0.6929% | 0.6949% | 1.204% | 1.195% | 2.216% | 1.339% | 1.274% | 1.212% | 1.424% | 1.357%
15 | 0.04155% | 0.002466% | 0.01197% | 0.02024% | 0.0301% | 0.03902% | 0.04758% | 0.05599% | 146.9% | 232.3% | - | - | 46.34% | 61.26% | - | -
16 | 0.04338% | 0.01326% | 0.01341% | 0.01051% | 0.01319% | 0.01333% | 0.01348% | 0.01336% | 284% | 311.4% | 41.22% | 45.14% | 28.28% | 20.11% | 15.18% | 11.83% | - | 0.08% | 0.02% | 0.02667% | 0.005% | 0.032% | 0.006667% | 0.008571% | - | 45.64% | 2.535% | 7.486% | 10.66% | 11.74% | 12.58% | 13.21%
17 | 0.02645% | 0.01262% | 0.003192% | 0.00515% | 0.01502% | 0.02386% | 0.0325% | 0.04088% | 380% | 540% | 340% | 188.2% | - | - | 69.47% | 49.77%
18 | 0.05316% | 0.01461% | 0.02296% | 0.03131% | 0.04175% | 0.0501% | 0.06054% | 0.06809% | 0.5847% | 0.6148% | 0.5434% | 0.4577% | 0.6662% | 0.5823% | 0.8067% | 0.708%
19 | 0.0004024% | 0.04689% | 0.03573% | 0.02903% | 0.01786% | 0.008932% | 1.19e-14% | 0.1148% | 0.3019% | 0.3311% | 0.2567% | 0.4582% | 0.3795% | 0.5797% | 0.5111% | 0.4185%

## HIL 603 small Ts (3)
These measurements are for a model with mutual inductance in the transmission lines
Ts = 200e-6
MATPOWER - No snubbers | [6 empty] | TYPHOON HIL | [8 empty] | Error
Bus data | [6 empty] | Bus data | [8 empty] | Voltage
Bus | Voltage |  | Generation |  | Load |  | Bus | Voltage |  |  |  | Generation |  | Load |  | Mag | Angle
# | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr) | # | Zone Base | Meas (V) | Mag (pu) | Angle (°) | P (MW) | Q (MVAr) | P (MW) | Q (MVAr)
1 | 1 | 0 | 2.47 | 3.16 |  |  | 1 | 7967.4337 | 7968.42 | 1.0001 | 0 | 2.6357 | 2.8316 |  |  | 0.01238% | - | -5.853% | -10.39%
2 | 0.998 | 0.026 |  |  |  |  | 2 | 7967.4337 | 7960.47 | 0.99913 | 0 |  |  |  |  | 0.1128% | -
3 | 0.996 | -0.001 |  |  |  |  | 3 | 7967.4337 | 7954.21 | 0.99834 | 0 |  |  |  |  | 0.235% | -
4 | 0.993 | -30.182 |  |  |  |  | 4 | 277.1281 | 273.358 | 0.9864 | -30.241 |  |  |  |  | 0.6651% | 0.1955%
5 | 0.985 | -30.848 |  |  |  |  | 5 | 277.1281 | 273.744 | 0.98779 | -30.241 |  |  |  |  | 0.2831% | 1.968%
6 | 0.952 | -31.248 |  |  |  |  | 6 | 277.1281 | 269.932 | 0.97403 | -31.6695 |  |  |  |  | 2.314% | 1.349%
7 | 0.985 | -0.1 |  |  |  |  | 7 | 7967.4337 | 7919.34 | 0.99396 | 0 |  |  |  |  | 0.91% | -
8 | 0.985 | -0.102 |  |  |  |  | 8 | 7967.4337 | 7919.25 | 0.99395 | 0 |  |  |  |  | 0.9089% | -
9 | 0.983 | -30.251 |  |  |  |  | 9 | 120.0889 | 118.172 | 0.98404 | -30.241 |  |  |  |  | 0.1056% | 0.03306%
10 | 0.981 | -0.132 |  |  |  |  | 10 | 7967.4337 | 7908.96 | 0.99266 | 0 |  |  |  |  | 1.189% | -
11 | 0.964 | -31.746 |  |  |  |  | 11 | 2401.7771 | 2360.56 | 0.98284 | -30.737 |  |  |  |  | 1.954% | 3.178%
12 | 0.951 | -62.801 |  |  |  |  | 12 | 277.1281 | 268.068 | 0.96731 | -61.9105 |  |  |  |  | 1.715% | 1.418%
13 | 0.954 | -62.556 |  |  |  |  | 13 | 277.1281 | 269.176 | 0.97131 | -60.4819 |  |  |  |  | 1.814% | 3.316%
14 | 0.963 | -31.757 |  |  |  |  | 14 | 2401.7771 | 2359.68 | 0.98247 | -31.6695 |  |  |  |  | 2.022% | 0.2755%
15 | 0.999 | 0.113 |  |  |  |  | 15 | 7967.4337 | 7958.78 | 0.99891 | 0 |  |  |  |  | 0.008622% | -
16 | 1 | 0.336 | 1.5 | -1.05 |  |  | 16 | 7967.4337 | 7951.31 | 0.99798 | 0 | 1.5 | -1.05 |  |  | 0.2024% | - | 0.001857% | -0.002333%
17 | 0.999 | 0.112 |  |  |  |  | 17 | 7967.4337 | 7958.05 | 0.99882 | 0 |  |  |  |  | 0.01779% | -
18 | 0.998 | -29.921 |  |  |  |  | 18 | 277.1281 | 276.681 | 0.99839 | -28.7952 |  |  |  |  | 0.03873% | 3.763%
19 | 0.933 | -30.695 |  |  |  |  | 19 | 277.1281 | 269.021 | 0.97075 | -33.1153 |  |  |  |  | 4.046% | 7.885%
|  |  | 3.97 | 2.11 | [7 empty] | 4.1357 | 1.7816 |  |  |  |  | -9.303% | -15.57%